SECTION 27 21 29

DATA COMMUNICATIONS SWITCHES AND HUBS

Copyright 2025 Allied Telesis Incorporated - All rights reserved.

<THIS ENTIRE DOCUMENT can be edited to meet specific client and project needs>

- GENERAL

SECTION INCLUDES

NETWORK SWITCHES

AT-x540L-28XTm (HV-x540L-28XTm)

  - GENERAL REQUIREMENTS

The specified network switch product shall be a switching/routing platform designed for use in an appropriate network system.

  - PROPOSAL SUBMITTALS

Follow all requirements noted on the Form of Proposal and head-end bidding documents if provided.

System Integrator shall provide the following submittals as part of the project submittal package.

Complete product and technical data specification data sheets that include all material and equipment and shall be available freely online. Include any installation manual(s) and warranty information.

A bill of material of all equipment with counts, part numbers and manufacturer.

Software manufacturer, name, and version.

New or additional feature licenses.

Third-party software if required by the project.

Locations and details for all components to be installed under this scope of work.

Placement Diagram showing the proposed location of all system hardware devices.

System Calculation of all network bandwidth and power requirements to ensure proper planning of networking infrastructure, based on the requirements outlined within these specifications.

features to meet or exceed the products named before bid submittal and with pre-approval.

PRE-CONSTRUCTION SUBMITTALS

After the project award, the contractor shall provide any additional submittals not included in their original pre-bid submittal package.

Product Data: For each type of product indicated. Include dimensions and data on features, performance, electrical characteristics, ratings, and finishes.

Location Drawings: For network infrastructure. Include plans, elevations, sections, details, and attachments to other work.

CLOSEOUT SUBMITTALS

After project completion, the contractor shall provide additional project close out submittals required.

Operation and Maintenance Data: For switches, routers, power supplies, access points, media converters, small form factor pluggables, to include in emergency, operation, and maintenance manuals.

Lists of spare parts and replacement components recommended to be stored at the site for ready access (if applicable).

Complete hardcopy printout and electronic copy from the equipment manufacturer which outlines system and equipment configuration, includes model number, IP address, and MAC address at the time of installation and other system settings.

DISCLOSURE OF NON-CONFORMING EQUIPMENT

Project owner desires to make an informed decision regarding the Contractor's proposed project approach, mobilization, staging and overall implementation schedule of tasks.

The contractor is required to disclose, separate from any cut or advertising sheets, any functional, operational, or electrical requirements of these specifications that they are not able to perform, and/or which fall outside the scope of their quotation.

ONGOING SUPPORT AND WARRANTY

    - The product manufacturer shall provide a limited lifetime warranty for the switch, to be free of defects in material and workmanship for the lifetime of the product.

DELIVERY, STORAGE, AND HANDLING

Deliver and store products in manufacturer's unopened packaging bearing the brand name and manufacturer's identification until ready for installation.

Handling: Handle materials to avoid damage.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's recommended limits.

SEQUENCING

Ensure that products of this section are supplied to affected trades in time to prevent interruption of construction progress.

RELATED SECTIONS

Division 28 - Electrical.

REFERENCES

Code of Federal Regulations (CFR).

Institute of Electrical and Electronics Engineers (IEEE):

802.3 Ethernet Standards.

International Electrotechnical Commission (IEC).

Federal Communications Commission (FCC):

FCC Rules and Regulation of Title 47 of CFR Part 15 Subpart B Class A.

Underwriters Laboratories (UL):

UL listed.

United States Military Standard (MIL-STD):

MIL-STD-810F - Environmental Engineering Considerations and Laboratory Tests.

National Defense Authorization Act (NDAA):

A series of United States of America Federal Laws that include equipment sourcing guidance and standards.

DEFINITIONS

Abbreviations:

ARP - Address Resolution Protocol.

NTP - Network Time Protocol.

PPPoE - Point to Point Protocol over Ethernet.

POE – Power Over Ethernet

RTP - Real-Time Transport Protocol.

RTCP - Real-Time Control Protocol.

RTSP - Real-Time Streaming Protocol.

SFP – Small Form-factor Pluggable

SMTP - Simple Mail Transfer Protocol.

SNMP - Simple Network Management Protocol.

SSL - Secure Sockets Layer.

TCP - Transmission Control Protocol.

UDP - User Datagram Protocol.

UPnP - Universal Plug and Play.

- PRODUCTS

MANUFACTURERS

Acceptable Manufacturer:

Allied Telesis Incorporated, which is located at: 10521 19th Ave SE, Suite 200 Everett, WA 98208

Phone: (408) 519-8700

Web: https://www.alliedtelesis.com/

Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.

NETWORK SWITCHES

AT-x540L-28XTm

EQUIPMENT

Manufacturer: 	Allied Telesis Incorporated

Model		AT-x540L-28XTm

Alternates: 	None

GENERAL SPECIFICATIONS

The managed switch shall be an AT-x540L-28XTm model.

The switch features 24 fixed 100M/1/2.5/5/10 G Base-T electrical ports.

The switch features 4 shared 1/10 G SFP+ slots.

The switch shall support the Ethernet data IEEE 802.3 protocol using Auto-negotiating and Auto-MDI/MDI-X features.

The switch shall provide Fault, Power, VCS, USB, and Link / Act status indicating LEDs for monitoring proper system operation.

The switch shall provide an RJ45 serial connection for local management of the device.

DATA SPECIFICATIONS

Data Interface: Ethernet IEEE 802.3bz

Data Rate:

Port1 to Port24: 100M/1/2.5/5/10 Gbps

Port25 to Port28 SFP+: 1/10 Gbps

Data Inputs: 28

Operation Mode: Simplex or Duplex

STATUS INDICATORS

System

Fault LED: Off – System is operating normally; Steady red – Firmware is loading; Flashing red (one time) – System or fan error; Flashing Red (six times) – Temperature exceeds thresholds

Power LED: Off – Switch is not receiving power; Steady green – Switch is operating normally.

VCS LED: Off – VCStack feature is disabled or unit is a “member” switch; Steady green – Unit is VCStack “master” switch.

USB LED: Off – No activity on USB port; Steady green – USB drive is attached; Flashing green – Information is being exchanged with USB Drive; Flashing amber – USB Drive error.

BASE-T Interface (port1 to port24)

Link/Activity: Off – Port has not established a link, or ecofriendly feature is enabled; Flashing green - Rx or Tx activities at 2.5/5/10Gbps; Steady green - Port has established a link and is active (2.5/5/10Gbps); Flashing amber - Rx or Tx activities at 100Mbps or 1Gbps; Steady amber- Port has established a link and is active (100Mbps or 1Gbps).

SFP Interface (port25 to port28)

SFP: Off - Port has not established a link, or the ecofriendly feature is enabled; Flashing green - Rx or Tx activities at 10Gbps; Steady green - SFP transceiver has established a link at 10Gbps, Flashing amber - Rx or Tx activities at 1000Mbps; Steady amber- Port has established a link and is active (1000Mbps).

CONNECTORS

Ethernet Port: RJ45

Optical: SFP+ slot

Console: RJ45

USB Type A

Power: C13 socket

ELECTRICAL SPECIFICATIONS

Power characteristics:

Voltage Input:100 to 240 VAC, 50/60 Hz

Current: 2A max

Power Consumption: Maximum 160 watts

MECHANICAL SPECIFICATIONS

Surface Mount Dimensions: 17.3” x 11.4” x 1.7” (440 mm x 290 mm x 44 mm)

Finish: Module shall be constructed of a metal enclosure.

Weight < 8.8 lbs. / 4000 g

ENVIRONMENTAL SPECIFICATIONS

MTBF: > 250,000 Hrs @25˚ C, 220,000 Hrs @30˚ C

Operating Temp: 0 to +50˚ C

Storage Temp: –25 to +70˚ C

Relative Humidity: 5 to 90% (non-condensing).

REGULATORY AGENCIES/APPROVALS AND LISTINGS

EMC:

ETSI EN300-386

EN300-132-2

FCC class A

VCCI class A

EMC (Immunity):

EN55024

EN61000-3-levels 2 (Harmonics), and 3 (Flicker) – AC models only

Safety:

UL60950-1

CAN/CSA-C22.2 No. 60950-1-03

EN60950-1

EN60825-1

AS/NZS 60950.1

Compliance Marks:

UL

cUL

FIPS 140-2

Restrictions on Hazardous Substances (RoHS) Compliance

EU RoHS compliant

China RoHS compliant

ACCESSORIES

Power cable x 1

Power cable hook x 1

Screws for attachment to equipment bracket x 6

Equipment Rack bracket x 2

Rubber bumper feet x 4

- EXECUTION

PREPARATION

System Integrator: Confirm the solution proposal planning and design with the installing contractor.

The network design and configuration to be verified for compatibility and performance with the input/output devices.

- 3.2	NETWORK SYSTEM INSTALLATION, NECESSARY MOUNTING ACCESSORIES, AND PROGRAMMING

    - PREPARATION

      - Installation of equipment in standalone, wall, or equipment rack configurations shall comply with equipment Installation guide, freely available on the manufacturer’s website.

      - Accessories for installation of equipment in wall or equipment rack configurations shall be installed according to the equipment installation guide.

      - Contractor personnel must comply with all applicable state and local licensing requirements.

    - CONFIGURATION

      - Configuration of equipment shall be conducted through

        - Serial management port (as applicable)

        - IP Terminal management session (SSH/Telnet)

        - Web GUI (as applicable)

        - Allied Telesis management software (as applicable)

      - Initial configuration shall include at minimum

        - Creation of individual administrator accounts with secure passwords per industry best practices.

        - Removal of default password.

        - Application of latest firmware updates.

        - Assign IP address and hostname.

        - Creation and assignment of backup configuration file

    - POST CONFIGURATION

      - As applicable, equipment shall be monitored for appropriate POE power budget utilization as client/edge equipment is connected.

      - Testing shall be conducted to ensure cabling meets performance standards outlined in equipment specifications

        - Testing can be performed internally by select network switches supporting the Cable Fault Locator (TDR) feature. Further information shall be referenced in the equipment configuration guide, available from the manufacturer.

- 3.3	CYBER SECURITY PROTECTION

    - All equipment requiring users to log on using a password to be configured with user/site-specific password/passwords. No system/product default passwords shall be allowed. Contractor shall implement all network manufacturer’s cyber security recommendations and configurations, following industry best practices per the equipment manufacturer configuration guide.

Document that all network switches do not have a default password.

Document that all network switches have the latest firmware (cyber security patches) installed.

Latest firmware updates shall be provided to contractor through the manufacturer software download portal.

Latest firmware updates shall be applied biannually or as recommended by the equipment manufacturer.

Evaluation of security best practices shall be conducted at minimum, concurrent to firmware updates. Evaluations shall include at minimum:

Review of admin access list to any equipment or management software.

Removal of any default passwords

Confirmation of appropriate equipment environmental state including history of temperature events.