Hanwha Techwin is a global leading supplier of solutions for IP and analog video surveillance. Building on the company's history of innovation, Hanwha Techwin is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-effectiveness. Hanwha Techwin is committed to the continued development of innovative systems products for professional security applications.

For additional information, visit http://www.hanwha-security.com/

2MP NETWORK AI IR VANDAL DOME CAMERA

# DIVISION 28 – ELECTRONIC SAFETY AND SECURITY

Notes to Specifier:

1. Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold text>.

2. Explanatory notes and comments are presented in colored text.

Important:  See further notes on the following page.

# Important Note to Security Systems Specifiers

# CSI MasterFormat 2016 incorporates numerous significant changes affecting electronic safety and security. This document is written to provide flexibility in using either format, although adoption of MasterFormat 2016 is encouraged. The following is a guide to the MasterFormat numbers relevant to the product referenced in this specification.

# Primary Specification Area:

# MasterFormat 2014:

28 20 00 	Electronic Surveillance

28 23 00 	Video Surveillance

28 23 29	Video Surveillance Remote Devices and Sensors

MasterFormat 2016:

# 28 20 00	Video Surveillance

# 28 2x xx	Surveillance Cameras

# 28 2x xx	IP Cameras

# Related Requirements:

# MasterFormat 2014:

# 27 20 00	Data Communications

# 28 23 13	Video Surveillance Control and Management Systems

# 28 23 16	Video Surveillance Monitoring and Supervisory Interfaces

# 28 23 19	Digital Video Recorders and Analog Recording Devices

# 28 23 23	Video Surveillance Systems Infrastructure

# MasterFormat 2016

# 27 15 01.xx	Video Surveillance Communications Conductors and Cables

# 27 20 00 	Data Communications

# 28 05 xx.xx	PoE Power Sources for Electronic Safety and Security

# 28 05 xx	Storage Appliances for Electronic Safety and Security

# 28 05 xx.xx	Network Video Recorders

# 28 05 xx	Cyber Requirements for Electronic Safety and Security

# 28 05 xx	Safety and Security Network Communications Equipment

# 28 2x 00	Video Management System

2MP NETWORK AI IR VNADAL DOME CAMERA

- GENERAL

  - SUMMARY

    - Section includes a 2MP IP video camera

    - Product - A 2MP IP video camera in in an IK10 rate dome body with IR illuminator.

    - Related Requirements

Refer to MasterFormat notes at the beginning of this document to select requirements specific to the MasterFormat version being used in the specification.

  - REFERENCES

    - Abbreviations

      - AGC		Auto Gain Control

      - AES		Advanced Encryption Standard

      - AI		Artificial Intelligence

      - API		Application Programming Interface

      - ARP		Address Resolution Protocol

      - AWB		Auto White Balance

      - BLC		Back light compensation

      - CBR		Constant Bit Rate

      - CVBS		Composite Video Blanking and Sync

      - DHCP		Dynamic Host Configuration Protocol

      - DNR		Digital Noise Reduction

      - DNS		Domain Name Server

      - DDNS		Dynamic Domain Name Server

      - DSCP		Differentiated Services Code Point

      - FPS		Frames Per Second

      - FTP		File Transfer Protocol

      - GOV		Group of Video

      - GUI		Graphical User Interface

      - HD		High Definition

      - HTTP		Hypertext Transfer Protocol

      - HTTPS		Secure HTTP

      - ICMP		Internet Control Message Protocol

      - IGMP		Internet Group Management Protocol

      - IP		Internet Protocol

      - IR		Infrared

      - JPEG		Joint Photographic Experts Group

      - LAN 		Local Area Network

      - LED		Light Emitting Diode

      - LDC		Lens Distortion Correction

      - LLDP		Link Layer Discovery Protocol

      - LPR		License Plate Recognition

      - MJPEG		Motion JPEG

      - MP		Megapixel

      - MPEG		Moving Pictures Experts Group

      - NAS		Network Attached Storage

      - NTP		Network Time Protocol

      - NVR		Network Video Recorder

      - PIM-SM	Protocol Independent Multicast-Sparse Mode

      - PoE		Power over Ethernet

      - PPPoE		Point to Point Protocol over Ethernet

      - QoS		Quality of Service

      - RTP		Real-Time Transport Protocol

      - RTCP		Real-Time Control Protocol

      - RTSP		Real-Time Streaming Protocol

      - SDK		Software Development Kit

      - SFP		Small Form factor Pluggable

      - SMTP		Simple Mail Transfer Protocol

      - SNMP		Simple Network Management Protocol

      - SSDR		Super Smart Dynamic Range

      - SSNR		Super Smart Noise Reduction

      - SSL		Secure Sockets Layer

      - TCP		Transmission Control Protocol

      - UDP		User Datagram Protocol

      - UPnP		Universal Plug and Play

      - VBR		Variable Bit Rate

      - VMS		Video Management System

      - WDR		Wide Dynamic Range

    - Reference Standards

      - Network - IEEE

        - 802.3 Ethernet Standards

        - 802.1x  Port-based Network Access Control

        - IPv4 IP addressing version 4

        - IPv6 IP addressing version 6

        - QoS Quality of Service

      - Video

        - ISO / IEC 23008-2:2013, MPEG-H Part2 (ITU H.265, HEVC)

        - ISO / IEC 14496–10, MPEG-4 Part 10 ( ITU H.264)

        - ISO / IEC 10918 – JPEG

        - ONVIF – Profile S / G / T

      - EMC & Safety

        - FCC 47 CFR Part 15 Subpart B

          - ANSI C63.4-2017 Class A

        - IC Regulation ICES-003 Issue7

          - CAN/CSA CISPR 32-17 Class A

        - CE EMC-Directive 2014/30/EU and 2011/65/EU

          - EN 55032:2015/A11:2020

          - EN 50130-4:2011

          - EN 610003-2:2014

          - EN 610003-3:2013

        - VCCI-CISPR 32:2016 Class A

        - AS/NZS CISPR32:2015 Class A

        - UL listed

        - CE EN 50581:2012 (hazardous substances)

      - Ingress Protection and Vandal Resistance

        - 60529:2006 – Degrees of Protection Provided by Enclosures – IP66/IP67

        - IEC EN 62262:2005 - Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts : IK10

        - NEMA 250-2014 – Enclosures for Electrical Equipment : NEMA 4X

    - Definitions

      - GOV (Group of Video object planes) – A set of video frames for H.264 and H.265 compression, indicating a collection of frames from the initial I-Frame (key frame) to the next I-Frame. GOV consists of two kinds of frames in video surveillance setup: I-Frame and P-Frame.

      - Dynamic GOV – Dynamic assignment of GOV length based on the complexity of the scene to efficiently manage bitrate of the video stream and reduce the storage required.

      - Multi-exposure wide dynamic range – Operation which automatically adjusts shutter speed to provide a wide range between dark and light areas visible at the same time, preventing backlighting issues. Long exposure is used for dark areas and a short exposure is used in bright areas.

      - Dynamic FPS – Dynamic assignment of FPS (frames per seconds) based on the movement of object(s) in the scene to efficiently manage bitrate of the video stream and reduce the storage required.

      - Smart Codec – Smart Codec that controls quantization parameter and dynamic FPS in H.265 and H.264 to efficiently manage bitrate of the video stream and reduce the storage required.

      - WiseStream Ⅰ/Ⅱ – Technology that controls quantization parameter, FPS, and GOV length in H.265 and H.264 to efficiently manage bitrate of the video stream and reduce the storage required.

      - WiseStream Ⅲ – Camera should be able to intelligently separate the objects from the background, and to keep the compression ratio low for classifying humans and vehicles.

      - WiseNR Ⅱ – Camera should be able to intelligently suppress the image noise and blurring to get clearer image when there are movements of detected objects such as humans or vehicles.

      - AI Prefer shutter – Camera should be able to intelligently control the shutter speed to obtain clearer image and to suppress image blurring when there are movements of detected objects such as humans or vehicles.

      - LDC – Lens Distortion Correction corrects image distortion at the edge of a wide angle lens. Since Fill mode maintains the screen’s top and bottom angular fields of view, the left and right end of the video could be cropped. Since Stretch mode maintains the screen’s top/bottom/left/right angular fields of view, none of the areas in the original video recording is lost, but the aspect ratio of the video is not maintained.

      - DORI (Detect, Observe, Recognize, Identify) – A standard system (EN-62676-4) for defining the ability of a camera to distinguish persons or objects within a covered area.

        - Detect: 25PPM / 8PPF

        - Observe: 63PPM / 19PPF

        - Recognize: 125PPM / 38PPF

        - Identify: 250PPM / 76PPF

  - SUBMITTALS

    - Product Data

      - Manufacturer’s printed or electronic data sheets

      - Manufacturer’s installation and operation manuals

      - Warranty documentation

  - QUALIFICATIONS

    - Manufacturer shall have a minimum of five years’ experience in producing IP video equipment.

    - Installers shall be trained and authorized by the Manufacturer to install, integrate.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.

    - Store the camera in a temperature environment specified in section 2.04 Detailed Specification, protected from mechanical and environmental conditions as designated by the manufacturer.

  - WARRANTY, LICENSING AND SUPPORT

    - Manufacturer shall provide at least a limited 3 year warranty for the product to be free of defects in material and workmanship.

    - Manufacturer shall provide embedded camera video analytics free of license charges.

END OF SECTION

- PRODUCTS

  - EQUIPMENT

    - Manufacturer: 	Hanwha Techwin

http://www.hanwha-security.com/

    - Model		XNV-C6083R

    - Alternates: 		None

  - GENERAL DESCRIPTION

    - Video Compression and Transmission – The camera shall have the following properties relating to the video signals it produces.

      - H.265, H.264 and MJPEG compression, each derived from a dedicated encoder and capable of being streamed independently and simultaneously.

        - H.265 and H.264 – maximum of 30/25fps(60Hz/50Hz) at all resolution

        - MJPEG – maximum of 15fps/12fps(60Hz/50Hz)

      - The camera shall be able to configure up to 10 independent video stream profiles with differing encoding, quality, frame rate, resolution, and bit rate settings.

      - The camera shall be able to configure various resolution selections.

        - 16:9 aspect ratio : 1920x1080, 1280x720, 800x448, 640x360

        - 4:3 aspect ratio :  1280x960, 1024x768, 800x600, 640x480, 320x240

        - 5:4 aspect ratio :  1280x1024, 720x576

        - 3:2 aspect ratio :  720x480

      - The camera shall support unicast video streaming up to 20 users.

      - The camera shall support multicast video streaming.

      - The camera shall support multiple video streaming up to 10 profiles.

      - The camera shall support 3 virtual channel support.

      - The camera shall be able to configure Dynamic DNS (DDNS). DDNS shall be provided with no additional cost by the manufacturer.

      - The camera shall provide WiseStream Ⅱ/Ⅲ, Dynamic GOV and Dynamic FPS to efficiently manage bit rate of the video stream and reduce storage.

      - The camera shall provide WiseNRⅡ that working based on AI engine for reduce noise and blur on image.

    - Camera – The camera device shall have the following physical and performance properties:

      - IK08 rated for protection against impacts.

      - True day/night operation with scheduling and options for external devices.

        - Low light level operation to 0.011 lux(30fps/25fps)/0.022lux(60fps/50fps) at F1.4 in color mode, 0.0011 lux(30fps/25fps)/0.0022lux(60fps/50fps) in black and white mode..

        - Black and white mode operation to 0 lux with IR LED on.

      - The camera shall be able to produce clear images in highly contrast scenes with multi-exposure wide dynamic range up to 150Db.

      - The camera shall be able to produce clear images in highly contrast scenes with multi-exposure wide dynamic range.

      - The camera shall be able to configure 32 privacy masking areas with quadrangle zones.

      - The camera shall have the defog feature to remove fogginess of scene which can be triggered automatically from the fog detection event.

      - The camera shall provide video display on smart phone (iPhone, Android) to adjust viewing angle, rotation and focus.

    - Intelligence and Analytics – The camera shall have a suite of intelligent analytic functions.

      - Analytics events based on AI engine : Object detection

(Person/Face/Vehicle(car/truck/bus/bicycle/motorcycle)/License plate), IVA(Virtual line/Area, Enter/Exit, Loitering, direction, intrusion)

      - Analytics events : Defocus detection, Motion detection, Tampering, Fog detection, Audio detection, Sound classification, Shock detection, Appear/Disappear

        - Motion detection with 8 definable detection areas with 8 point polygonal zones, and minimum/maximum object size.

        - Detection and classification of the following sound.

          - Scream

          - Gunshot

          - Explosion

          - Crashing glass

      - Business Intelligence : People counting, Queue management, Heatmap(based on AI engine)

    - Interoperability – The camera shall be ONVIF Profile S / G and T compliant.

    - The camera shall possess the following further characteristics:

      - Micro SD/SDHC/SDXC memory card with configurable pre-alarm and post-alarm recording intervals

      - NAS recording option with configurable pre-alarm and post-alarm recording intervals

      - Alarms and notifications

        - alarm notification triggers:

          - Analytics

          - Network disconnect

          - Alarm input

          - App event

          - Time schedule

        - available notification means upon trigger:

          - File upload(image) : e-mail/FTP

          - Notification : e-mail

          - Recording : SD/SDHC/SDXC or NAS recording at event triggers

          - Alarm output

          - Handover(PTZ preset, Send message by HTTP/HTTPS/TCP)

          - Audio clip playback

      - Pixel Counter available in the web viewer.

      - IP52/IK08

      - This device has been verified using STP cable. The use of appropriate GND grounding and STP cable is recommended to effectively protect your product and property from transient voltage, thunderstroke, communication interruption.

  - CAMERA SOFTWARE

    - The camera shall have a built in web server.

    - The web viewer shall provide a monitoring screen which displays live camera video and simultaneously provides same-screen access to the following functions:

      - Live view window size

      - Resolution setting

      - Image (snapshot) capture

      - Manual recording to SD or NAS

      - Audio/microphone control

      - Access recorded data playback and camera configuration menus

    - The web viewer shall provide a playback screen which provides access to the following functions:

      - Recorded data search using date and time range

      - Recorded data search using event type

      - Play a recorded video by event triggering

      - Set playback speed

      - Play audio if present

      - Generate a backup copy of saved video data

    - The web viewer shall provide a setup screen which provides access to the following configuration settings and functions in the camera:

      - Digital video profile to include compression type, maximum or target bit rate, frame rate, multicast parameters, and crop encoding area

      - User profile to include password, access level, authentication

      - Date and time

      - Network settings and IP version

        - DDNS

        - IP filtering

        - SSL/TLS, including certificate management

        - 802.1x authentication

        - Quality of Service settings

        - SNMP to include version selection and settings

        - Auto IP configuration

      - Video setup

        - Flip / mirror mode

        - Video output type

        - Privacy zone

      - Audio setup to include source, audio codec type, gain and bit rate.

      - Camera settings to configure image preset, sensor frame capture, dynamic range, white balance, back light, exposure, day/night operation, on-screen display, sharpness, contrast, color level and lens distortion correction.

      - Event detection setup to configure notification parameters, recording rules, time schedule, tamper protection, motion detection and event triggers

      - System function to control reboot, upgrade, check system and event logs and application (SDK) management

      - View profile information

  - DETAILED SPECIFICATIONS

    - Video

      - Imaging device		1/2.8" CMOS

      - Scanning			Progressive

      - Minimum Illumination	Color: 0.011Lux(F1.4, 1/30sec, 30IRE), 30/25fps

B/W: 0.0011Lux(F1.4, 1/30sec, 30IRE), 0Lux(IR ILED On), 30/25fps

Color: 0.022Lux(F1.4, 1/30sec, 30IRE), 60/50fps

B/W: 0.0022Lux(F1.4, 1/30sec, 30IRE), 0Lux(IR ILED On), 60/50fps

      - Video out			USB : Micro USB Type B, 1280x720 for installation

    - Lens

      - Focal length		2.8~12mm(4.3x) motorized varifocal

      - Max. Aperture Ratio	F1.4(Wide) ~ ????????

      - Field of View		H: 119.5°(Wide)~27.9°(Tele)

V: 62.8°(Wide)~15.7°(Tele)

D: 142.1°(Wide)~32.0°(Tele)

      - Min. Object Distance	0.5m(1.64ft)

      - Focus Control		Simple focus, Manual

      - Lens Type			DC auto iris with hall sensor (IR corrected)

    - Pan & Tilt & Rotate

      - PTR Range		0°~360° / -45°~75° / 0°~355°

    - Operational Functions

      - IR Viewable Length		WiseIR 40m(131.23ft)

      - Camera Title 		Off / On (Displayed up to 85 characters)

      - Day/Night Setting		Auto (ICR) / Color / B/W / Schedule

      - Backlight Compensation	Off / BLC / HLC / extremeWDR(150dB)

      - Contrast Enhancement	SSDR

      - Digital Noise Reduction	WiseNRⅡ(Based on AI engine), SSNRⅤ

      - Digital Image Stabilization	Support (built-in gyro sensor)

      - Defog			Support

      - Motion Detection		Off / On (8ea, 8-point polygonal)

      - Privacy Masking		Off / On (32ea, Quadrangle zones)

- Color: Grey / Green / Red / Blue / Black / White

- Mosaic

      - Gain Control		Off / Manual / Max Gain

      - White Balance 		ATW / Narrow ATW / AWC / Manual / Indoor / Outdoor

      - LDC			Support (Fill/stretch mode)

      - Electronic Shutter Speed 	Min / Max / Anti-flicker (2 ~ 1/12,000sec)

Prefer shutter control (Based on AI engine)

      - Image Rotation		Flip: Off / On

Mirror: Off / On

Hallway view (90°/270°)

      - Digital PTZ		Support

      - Alarm I/O			2 configurable I/O ports

      - Alarm Triggers		Analytics, Network disconnect, Alarm input, App event,

Time schedule

      - Alarm Events		File upload(image): e-mail/FTP

Notification: e-mail

Recording: SD/SDHC/SDXC or NAS recording at event triggers

Alarm output

Handover (PTZ preset, Send message by HTTP/HTTPS/TCP)

Audio clip playback

      - Pixel Counter		Support

      - Storage			Micro SD/SDHC/SDXC 1slot 512GB

      - Analytics			Analytics events based on AI engine : Object detection

(Person/Face/Vehicle (car/truck/bus/bicycle/motorcycle)/

License plate),

IVA (Virtual line/Area, Enter/Exit, Loitering, direction, intrusion)

      - Business Intelligence	Based on AI engine : People counting, Queue management,

Heatmap

      - Analytics events		Defocus detection, Motion detection, Tampering, Fog detection,

Audio detection, Sound classification, Shock detection,

Appear/Disappear

      - Memory			2.8~12mm(4.3x) motorized varifocal

      - Max. Aperture Ratio	F1.4(Wide) ~ ????????

      - Field of View		H: 119.5°(Wide)~27.9°(Tele)

V: 62.8°(Wide)~15.7°(Tele)

D: 142.1°(Wide)~32.0°(Tele)

    - Video Streams

      - Video compression		H.265, H.264, MJPEG

      - Resolution			1920x1080, 1280x1024,1280x960, 1280x720, 1024x768, 800x600,

800x448, 720x576, 720x480, 640x480, 640x360, 320x240

      - Maximum Framerate

        - H.265 / H.264		Max. 60fps/35fps(60Hz/50Hz)

        - MJPEG 		Max. 30fps/25fps(60Hz/50Hz)

      - Smart Codec		Manual(5ea area), WiseStreamⅡ,

WiseStream Ⅲ	(Based on AI engine support)

      - Bitrate Control Method	H.265 / H.264: CBR or VBR

MJPEG: VBR

      - Streaming Capability	Unicast(20 users) / Multicast

Multiple streaming (Up to 10 profiles, 3 virtual channel support)

      - Streaming method		Unicast / Multicast

      - Simultaneous Users	20 maximum (Unicast)

      - Profile set			Max. 10 ea

      - Interoperability		ONVIF Profile S / G / T, SUNAPI (HTTP API),

Wisenet Open Platform

    - Audio

      - Audio In			Selectable(mic in/line in)

Supply voltage: 2.5V DC (4mA), Input impedance: 2K Ohm

      - Audio Out			Line out, Max. output level 1Vrms

      - Audio Compression		G.711 u-law /G.726 Selectable

G.726 (ADPCM) 8KHz, G.711 8KHz

G.726: 16Kbps, 24Kbps, 32Kbps, 40Kbps

AAC-LC: 48Kbps at 16KHz

    - Network

      - Connectivity 		Metal shielded RJ-45(10/100/1000BASE-T)

      - Protocol

        - IP v4 / v6, TCP, UDP

        - Configuration: DHCP, LLDP

        - Web service: HTTP, HTTPS

        - Network Service: ARP, Bonjour, DNS, ICMP, NTP, PIM-SM, SNMPv1/v2c/v3(MIB-2), UPnP

        - Media: RTP, RTCP, RTSP

        - Unicast: SRTP

        - Multicast: IGMP, PIM-SM

        - Notifications: FTP, SMTP

      - DDNS – The camera shall support DDNS services offered by the manufacturer and others publicly available service offerings

      - QoS – Layer 3 DSCP

      - Security Feature

        - UL-CAP Certified

        - User password protection

        - The device shall not provide a manufacture default password. Initial password setting shall be required to access the camera.

        - A minimal level of password complexity shall be required by the camera.

        - The camera shall not have a manufacture back-door password.

        - The manufacturer shall provide a tool that provides the ability to make password changes to multiple cameras at the same time.

        - IP address filtering – List of allowed or blocked IP addresses.

        - SRTP secured video communication for multicast.

        - Digest login authentication.

        - User access log.

        - 802.1X Authentication (EAP-TLS, EAP-LEAP)

        - Device Certificate (Hanwha Techwin Root CA)

        - HTTPS(SSL/TLS) login authentication and secured video communication with TLS v1.3

        - Disk encryption on SD card recording (AES-256)

        - File encryption on local disk recording via web browser (AES-256)

        - Mutual Authentication (Client Authentication) for secure communication

        - Secure OS and Security Boot

      - Discovery – The manufacturer shall offer a discovery program to identify all devices of them on the network.

      - Configuration – The manufacturer shall offer a configuration program that remotely allows users to change settings on multiple cameras simultaneously.

      - Firmware upgrade – The manufacturer shall offer a program capable of upgrading multiple cameras at the same time (not requiring access to individual cameras).

      - Camera backup setting – The manufacturer shall provide a program that provides the ability to save multiple camera settings to a file and restore these camera settings if needed.

      - Reporting – The manufacturer shall provide a tool that can generate a report including thumbnail view, MAC address, IP address, serial number and other camera settings.

    - Electrical

      - Power

        - Input Voltage			PoE(IEEE802.3af, Class3), 12VDC

        - Power Consumption		PoE: Max 12.95W, typical 11.2W

12VDC: Max 13.2W, typical 10.8W

    - Mechanical And Environmental

      - Color/Material			White / Aluminum

Hard-coated dome bubble

      - RAL Code				RAL9003

      - Dimensions (W x H)		Ø160x118mm(Ø6.30x4.65")

      - Weight 				1,450g(3.20 lb)

      - Compatible Conduit hole / Gangbox	1/2”(M20)

Single, double, 4” octagon, 4” square

      - Hanging Mount(Dome)		SBP-167HMW

      - Weater Cap(Dome)			SBV-161WCW

      - Temperature

        - Operating			-40 °C ~ 55 °C(40°F ~ +131°F)

* Maximum temperature: +60°C (intermittent)

* Start up should be done at above -20°C

NEMA TS-2: 74°C

        - Storage			-50°C ~ +60°C(-58°F ~ +140°F)

      - Humidity

        - Operating 			Less than 95% RH (non-condensing)

Humidity control /w GORE vent

        - Storage			Less than 90% RH (non-condensing)

      - Ingression Protection		IP66/IP67/NEMA4X

      - Vandal Resistance			IK10

    - DORI

      - Detect (25PPM/ 8PPF) 		Wide: 22.4m(73.47ft) / Tele: 154.6m(507.18ft)

      - Observe (63PPM/ 19PPF) 		Wide: 9.0m(29.39ft) / Tele: 61.8m(202.87ft)

      - Recognize (125PPM/ 38PPF) 	Wide: 4.5m(14.69ft) / Tele: 30.9m(101.44ft)

      - Identify (250PPM/ 76PPF) 		Wide: 2.2m(7.35ft) / Tele: 15.5m(50.72ft)

      - END OF SECTION

- EXECUTION

  - INSTALLERS

            - Contractor personnel shall comply with all applicable state and local licensing requirements.

  - PREPARATION

            - The network design and configuration shall be verified for compatibility and performance with the camera(s).

            - Network configuration shall be tested and qualified by the Contractor prior to camera installation.

            - All firmware found in products shall be the latest and the most up-to-date provided by the manufacturer, or of a version as specified by the provider of the VMS or NVR.

            - All equipment requiring users to log on using a password shall be configured with user/site-specific password/passwords. No system/product default passwords shall be allowed.

  - INSTALLATION

            - The contractor shall carefully follow instructions in documentation provided by the manufacturer to insure all steps have been taken to provide a reliable, easy-to-operate system.

            - All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

            - Before permanent installation of the system, the contractor shall test the system in conditions simulating the final installed environment.

  - STORAGE

            - The hardware shall be stored in an environment where temperature and humidity are in the range specified by the manufacturer.

END OF SECTION