GUIDE SPECIFICATION

Section 28 23 29

[image: image1.jpg]LW




Digital Watchdog is a leading manufacturer of security and surveillance solutions, offering stunning image quality, advanced hardware capabilities, reliable customer support and lowest total cost of deployment to the analog & IP megapixel surveillance markets. Located in Tampa, FL with manufacturing facilities in Seoul, Korea, Digital Watchdog is committed to delivering powerful security solutions to its customers worldwide.
For additional information, contact: 

Digital Watchdog, Inc., Inc.

5436 West Crenshaw Street 
Tampa, Florida 33634 USA

Phone: +1 813 888-9555

Web: www.digital-watchdog.com

E-mail: dw-tech@dwcc.tv
HIGH DEFINITION WEATHER RESISTANT BULLET VIDEO CAMERA
DIVISION 28 – ELECTRONIC SAFETY AND SECURITY
28 20 00 
Electronic Surveillance
28 23 00 
Video Surveillance

28 23 29
Video Surveillance Remote Devices and Sensors

Notes to Specifier:

1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold text>.
2.  Explanatory notes and comments are presented in colored text.

HIGH DEFINITION IP BULLET VIDEO CAMERA

PART 1   GENERAL

1.01 SUMMARY
A.  Section includes a 1080p high definition IP video camera in a weather-resistant bullet housing. 
B.  Product - A high definition video camera,  based on H.264, MPEG-4 and MJPEG compression, capable of streaming 30 fps at resolutions up to1920 x 1080, with dual streaming capability in a vandal resistant and IP66-rated weather-resistant bullet style housing.
C. Related Requirements
1. 27 20 00 Data Communications 

2. 28 23 13 Video Surveillance Control and Management Systems

3. 28 23 16 Video Surveillance Monitoring and Supervisory Interfaces

4. 28 23 19 Digital Video Recorders and Analog Recording Devices

5. 28 23 23 Video Surveillance Systems Infrastructure
1.02 REFERENCES
A. Abbreviations
1. AGC - Automatic Gain Control
2. ARP – Address Resolution Protocol
3. AWB  - Automatic White Balance
4. BLC – Back light compression

5. DHCP - Dynamic Host Configuration Protocol
6. DNR – Digital Noise Reduction
7. DNS - Domain Name Server
8. DDNS – Dynamic Domain Name Server
9. fps - frames per second
10. FTP - File Transfer Protocol
11. GUI – Graphical User Interface
12. HLC – Highlight Compensation
13. HTTP - Hypertext Transfer Protocol
14. ICMP – Internet Control Message Protocol
15. IGMP - Internet Group Management Protocol
16. IP - Internet Protocol
17. JPEG - Joint Photographic Experts Group
18. MJPEG - Motion JPEG
19. MPEG - Moving Pictures Experts Group
20. NTP - Network Time Protocol
21. PoE - Power over Ethernet
22. PPPoE - Point-to-Point Protocol over Ethernet
23. QoS – Quality of Service
24. RARP – Reverse Address Resolution Protocol
25. RTP - Real-Time Transport Protocol
26. RTSP - Real-Time Streaming Protocol
27. SMTP - Simple Mail Transfer Protocol
28. TCP - Transmission Control Protocol
29. UDP - User Datagram Protocol
30. VMS - Video Management System
31. WDR – Wide Dynamic Range
B. Reference Standards
1. Network

a. IEEE - 802.3 Ethernet Standards
2. Video

a. ISO / IEC 14496 – MPEG-4

1) ISO / IEC 14496–10, MPEG-4 Part 10 ( ITU H.264)

b. ISO / IEC 10918 – JPEG 
c. ONVIF – Profile S
3. Emissions
a. FCC-47 CFR Part 15 Class B
4. Environmental

a. ANSI / IEC60529 – Degrees of Protection Provided by Enclosures
b. International Electrotechnical Commission (IEC) – Ingress Protection Rating IP66

1.03 SUBMITTALS
A. Product Data
1. Manufacturer’s printed or electronic data sheets
2. Manufacturer’s installation and operation manuals
3. Warranty documentation

1.04 QUALIFICATIONS
A. Manufacturer shall have a minimum of five years’ experience in producing IP video equipment.
B. Installers shall be trained and authorized by the Manufacturer to install, integrate, test, and commission the system.
1.05 DELIVERY, STORAGE AND HANDLING

A. Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.

B. Store the camera in a temperature environment of -10° C to 50° C (14° F to 122° F), protected from mechanical and environmental conditions as designated by the manufacturer.

1.06 WARRANTY AND SUPPORT
A. Manufacturer shall provide a limited 2 year warranty for the product to be free of defects in material and workmanship.
END OF SECTION

PART 2  PRODUCTS

2.01 EQUIPMENT
A. Manufacturer: 
Digital Watchdog, Inc.



5436 West Crenshaw Street



Tampa, FL 33634 USA




Phone: +1 813 888-9555



Web: www.digital-watchdog.com



E-mail:  dw-tech@dwcc.tv
B. Models MB721M4TIR, MB721M8TIR Series
Digital Watchdog model differences:

MB721M4TIR
4 mm fixed lens

MB721M8TIR
8 mm fixed lens
C. Alternates: None

2.02 GENERAL DESCRIPTION

A. The High Definition Weather Resistant Bullet Camera (“IP bullet camera”) shall provide video performance capable of providing selectable resolutions up to 1920 x 1080 pixels at 30 frames per second (fps).
B. The IP bullet camera shall possess the following characteristics:
1. H.264, MPEG-4 and MJPEG compression
2. 2.1 megapixels

3. two independent IP video streams (dual streaming)

4. day/night operation with IR cut filter
5. 12 x digital zoom

6. Integral IR LED illuminator providing 50 foot distance
7. 16 privacy masking regions
8. integral motion detection

9. 3D digital noise reduction

10. PoE capable
11. multicast or unicast capable

12. local storage via Micro SD or SDHC card
13. Dynamic DNS (DDNS) support

14. IP-66 rated
2.03 VIDEO
A. Imager
1. Sensor:
 1/2.8" Sony CMOS
2. Minimum illumination

a. Color mode: 

<0.5 lux (F2.5 – 30IRE)> <2.4 lux (F2.0 (30 IRE)>
b. Black & white mode: 
<0.0 lux (F2.5 – 30IRE) > <.5 lux (F2.0 (30 IRE)>
3. Scanning - Progressive
4. Image Control Settings shall be available for:
a. Automatic white balance (AWB)
1) Selectable for Auto, Indoor, Preset, Auto External, or Manual
a) Manual mode to provide the ability to configure red offset, blue offset and warmth or coolness of light.

b. Exposure  modes: 
automatic or manual
1) In manual exposure mode, configurable settings for:

a) brightness

b) shutter mode: 
automatic or manual from 1/30 to 1/60000

c) digital slow shutter to decrease shutter speed in low light

d) AGC:

41 dB maximum
e) Backlight compensation (BLC)

f) Highlight compensation (HLC)

g) WDR level:

100 dB minimum
c. Day and night settings, to allow configuration for Day (color), Night (Black and White), or Automatic.

d. Frequency

e. Image sharpness

f. IR LED control

g. Chroma

h. Image mirror or flip

i. Digital noise reduction
j. Privacy zone definition, up to 16 zones
5. Lens
a. Lens type: 


<4.0 mm F1.8 > <8.0 mm F2.0> fixed
b. Shutter speed:  

1/30 to 1/60,000 sec
c. Horizontal Angle of View: 
 <86°>  <42°>  
Note: The above options pertain to the MB721M4TIR and MB721M8TIR, respectively.

B. Video Streams 
1. The IP bullet camera shall support two configurable video streams, each of which may have the following properties:
a. Resolution:
320 x 240 (4 x 3) to 1920 x 1080 (16:9)
b. Compression type:
1) H.264
2) MPEG-4
3) MJPEG
c. Bit rate:
1.8 Mbps – 8 Mbps
d. Frame rate:
0 – 30 fps
e. MJPEG image quality
C. Motion Detection – The IP bullet camera shall have the ability to detect motion within user defined areas of the video image.
1. Configuration settings shall be available for sensitivity and dwell time.
D. Storage and Recording
1. The IP bullet control shall have onboard SD card storage.
a. Card type:
Micro SDHC Class 10
b. Capacity:
4 GB – 32 GB
2. Local recording on the SD card shall commence upon loss of network connectivity, based on a pre-programmed schedule.
3. The local SD storage shall have the ability to be backed up to alternate media without removal of the SD card from the camera.
E. ONVIF – Video streams shall be capable of supporting ONVIF protocol, profile S.
F. Other
1. Single Images - The IP bullet camera shall support jpg file image screenshot and export.
2. Discovery - Manufacturer shall offer a discovery program to identify all devices of his manufacture on the network.
3. Emergency alarm – The IP bullet camera shall allow sending of a video clip of configurable duration to up to five server locations.
4. Access - The IP bullet camera shall permit up to five users to simultaneously access the camera.
2.04 NETWORK
A. Connectivity: 100 BASE-TX Ethernet with RJ-45 connector
B. Protocols supported

1. Transmission Control Protocol (TCP), Internet Protocol (IP) v4 and v6, User Datagram Protocol (UDP)
2. Configuration: Dynamic Host Configuration Protocol (DHCP)
3. Web services: Hypertext Transfer Protocol (HTTP) 

4. Network services: Domain Name System (DNS), Network Time Protocol (NTP)
5. Media: Real-Time Transport Protocol (RTP), Real-Time Streaming Protocol (RTSP)
6. Multicast: Internet Group Management Protocol (IGMP)

7. Notifications: File Transfer Protocol (FTP), Simple Mail Transfer Protocol (SMTP)
8. Remote Access: Point-to-Point Protocol over Ethernet) (PPPoE)
C. Flow Control –The IP bullet camera shall support TCP and Layer 3 QoS protocols to control network congestion.
D. DDNS – The IP bullet camera shall support DDNS services offered by the Manufacturer and other publicly available service offerings.
E. Security

1. The IP bullet camera shall support IP address filtering whereby users can enter a list of allowed or blocked IP addresses for viewing video and configuring camera settings
2. The IP bullet camera shall provide three levels of user access with password protection.
2.05 ADDITIONAL FEATURES

A. System Information
1. The system settings of the IP bullet camera shall be exportable as a separate file.
2. The IP bullet camera shall maintain an accessible log of system and motion-triggered events.

a. The log shall be exportable to an Excel spreadsheet file.
2.06 CAMERA SOFTWARE
A. The IP bullet camera shall have a built in web server which supports browser-based configuration using Internet Explorer, Google Chrome, Mozilla Firefox, Apple Safari.
B. The software GUI shall allow access to camera information and all primary software functions, including:
1. Camera network address

2. Configuration

3. Stream control

4. Screen snapshot, print and export

5. Start and stop recording
C. The Manufacturer shall offer video viewer and configuration to implement the following actions:
1. Camera discovery
2. Configuration 
a. video parameters
b. events and notifications

1) motion related

2) emergency

c. camera network parameters

d. SD card storage recording management 

e. image capture, export, and print
3. Viewer - view video streams through the web browser
4. Image print and export
5. Instant record and playback
6. Alerts
a. e-mail setup
b. define web addresses for notifications
7. System
a. firmware upgrade
b. reset to factory default
c. set date, time, and NTP server synchronization
d. user access control
e. view and export camera settings
f. view system logs
2.07 ELECTRICAL

A. Power

1. Sources

a. 12 VDC

b. PoE (IEEE 802.3af. 802.3at Class 2) - 48 VDC 

2. Power Consumption

a. IR LED off:
3.5 W, 290 mA
b. IR LED on:
5 W, 500 mA

B. Connectors

1. Ethernet: 


RJ-45 cable pigtail
2. External power (12 VDC): 
2-conductor power pigtail
2.08 MECHANICAL AND ENVIRONMENTAL

A. Housing Material: 

aluminum die-cast
B. Configuration: 

bullet
C. Environmental Rating: 
IP-66
D. Dimensions (L x D):  
6.41 in. x 2.51 in. (163 mm x 64 mm)
E. Temperature:

1. Operating: 

-10° C to 50° C (14° F to 122° F)
F. Humidity:


0 - 90%, non-condensing

END OF SECTION
PART 3    EXECUTION

3.01 INSTALLERS
A. Contractor personnel shall comply with all applicable state and local licensing requirements.
3.02 PREPARATION

A. The network design and configuration shall be verified for compatibility and performance with the camera(s).
B. Network configuration shall be tested and qualified by the Contractor prior to camera installation.
3.03 INSTALLATION
A. Before permanent installation of the system, the system shall be factory tested in conditions simulating the final installed environment

1. A report indicating successful test results shall be produced.
3.04 STORAGE

A. The IP bullet camera hardware shall be stored in an environment where temperature and humidity are in the range specified by the Manufacturer.
END OF SECTION

DWC-MB721M4TIR, DWC-MB721M8TIR

HIGH DEFINITION WEATHER RESISTANT BULLET CAMERA

August 2018

28 23 29 - 8

