April 2017

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on MasterFormat 2016 and The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section 28 21 00: Video Surveillance

Section 28 21 13: IP Cameras

12 MP IR BOX NETWORK CAMERA

- – GENERAL

  - SUMMARY

    - Section Includes

      - Section 28 21 17: Video Surveillance – Surveillance Cameras – Camera Housings

      - Section 28 21 19: Video Surveillance – Surveillance Cameras – Camera Mounts

      - Section 28 21 21: Video Surveillance – Surveillance Cameras – Illuminators

      - Section 28 27 00: Video Surveillance – Video Surveillance Sensors

    - Related Sections

      - [Section 28 33 15: Security Detection, Alarm and Monitoring – Security Monitoring and Control – Security Monitoring and Control Software].

**********Specifier’s note: Include those standards referenced elsewhere in this SECTION.

  - REFERENCES

    - Federal Communications Commission (FCC) (www.fcc.gov)

      - FCC Part 15 Subpart B

    - Underwriters Laboratories, Inc. (UL) (www.ul.com)

      - UL60950-1

    - HD standards

      - Complies with theUHD-1 Standard in:

        - Resolution: 3840 x 2160

        - Scan: Progressive

        - Color representation: complies with ITU-R BT.2020-2

        - Aspect ratio: 16:9

        - Frame rate: 25 and 30 frames/s

      - Complies with the SMPTE 274M-2008 Standard in:

        - Resolution: 1920x1080

        - Scan: Progressive

        - Color representation: complies with ITU-R BT.709

        - Aspect ratio: 16:9

        - Frame rate: 25 and 30 frames/s

      - Complies with the 296M-2001 Standard in:

        - Resolution: 1280x720

        - Scan: Progressive

        - Color representation: complies with ITU-R BT.709

        - Aspect ratio: 16:9

        - Frame rate: 25, 30, 50 and 60 frames/s

        - Interference-Causing Equipment Standards

      - Complies with SMPTE ST 2036-1:2013 Standard in:

        - Resolution: 3840 x 2160

        - Scan: Progressive

        - Color representation: complies with ITU-R BT.2020 (2012)

        - Aspect ratio: 16:9

        - Frame rate: 25 and 30 frames/s

  - SYSTEM DESCRIPTION

    - Section Includes

      - Video Surveillance – Surveillance Cameras – IP Cameras

    - Performance Requirements

      - The 12 MP Box camera shall be a full-featured Box camera designed for discrete video surveillance applications in indoor and outdoor environments.

      - The 12 MP Box camera shall feature Smart Scene Adaptive (SSA) intelligent image technology to automatically evaluate and compensate for changes in the luminance of a scene.

      - The 12 MP Box camera shall provide direct network connection using Smart H.265+, H.265, Smart H.264+, H.264, or MJPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The 12 MP Box camera shall offer a mechanical day/night IR cut filter that delivers color images during daylight and automatically switches to a monochrome image as the scene darkens.

      - The 12 MP Box camera shall utilize an algorithm that dynamically adjusts the cameras contrast settings to provide usable image quality in scenes affected by fog, smog, mist, smoke or other low contrast scene.

      - The 12 MP Box camera shall be a high performance 1/1.7-in. progressive scan day/night CMOS sensor with 12 MP resolution.

      - The 12 MP Box camera shall support the following dual, redundant power options:

        - 12 VDC or 24 VAC.

        - PoE (IEEE 802.3af, class 0).

        - The 12 MP Box camera shall default to use power from the PoE power supply, if connected.

        - The 12 MP Box camera shall reboot and switch to the 12 VDC or 24 VAC power supply if power from the PoE power supply is lost.

      - The 12 MP Box camera shall offer Digital Wide Dynamic Range for clear images in extreme high-contrast environments.

      - The 12 MP Box camera shall offer the Intelligent Video System to detect and analyze moving objects for improved video surveillance.

      - The 12 MP Box camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.

      - The 12 MP Box camera shall offer three separate and configurable streams with individually configurable 12 MP, 4K and Full HD streams.

  - SUBMITTALS

    - Submit under provisions of Section [01 33 00.]

    - Product Data:

      - Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.

    - Dimensional Drawings; include

      - Overall device dimensions.

      - Dimensions specific for installation.

    - Closeout Submittals

      - User manual.

      - Parts list.

      - Maintenance requirements.

  - QUALITY ASSURANCE

    - Manufacturer:

      - Minimum of [10] years of experience in manufacture and design Video Surveillance Devices.

    - Video Surveillance System:

      - List certifying bodies (UL, CSA, etc.)

      - Provide evidence of compliance upon request.

    - Installer:

      - Minimum of [5] years of experience installing Video Surveillance System.

  - DELIVERY, STORAGE AND HANDLING

    - Comply with requirements of Section 01 60 00.

    - Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.

    - Protect store materials from environmental and temperature conditions following manufacturer’s instructions.

    - Handle and operate products and systems according to manufacturer’s instructions.

  - WARRANTY

    - Provide manufacturer’s warranty covering [2] years for replacement and repair of defective equipment. Warranty varies country to country.

  - MAINTENANCE

    - Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.

    - Provide factory direct technical support via phone and e-mail.

- – PRODUCTS

  - MANUFACTURERS

    - [Acceptable Manufacturer:

Dahua Technology USA Inc.

23 Hubble, Irvine, CA 92618

Tel: (949) 679-7777

Fax: (949) 679-5760

Email: sales.usa@global.dahuatech.com]

    - Substitutions: [Not permitted.] [Under provisions of Division 1.]

      - [All proposed substitutions must be approved by the Architect or Engineer professional.]

      - [Proposed substitutions must provide a line-by-line compliance documentation.]

  - 12 MP BOX NETWORK CAMERA NK8BA4

    - General Characteristics:

      - The 12 MP Box camera shall be a full-featured Box camera designed for discrete video surveillance applications in indoor and outdoor environments.

      - The 12 MP Box camera shall feature Smart Scene Adaptive (SSA) intelligent image technology to automatically evaluate and compensate for changes in the luminance of a scene.

      - The 12 MP Box camera shall provide direct network connection using Smart H.265+, H.265, Smart H.264+, H.264, or MJPEG compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.

      - The 12 MP Box camera shall offer a mechanical day/night IR cut filter that delivers color images during daylight and automatically switches to a monochrome image as the scene darkens.

      - The 12 MP Box camera shall utilize an algorithm that dynamically adjusts the cameras contrast settings to provide usable image quality in scenes affected by fog, smog, mist, smoke or other low contrast scene.

      - The 12 MP Box camera shall be a high performance 1/1.7-in. progressive scan day/night CMOS sensor with 12 MP resolution.

      - The 12 MP Box camera shall support the following dual, redundant power options:

        - 12 VDC or 24 VAC.

        - PoE (IEEE 802.3af, class 0).

        - The 12 MP Box camera shall default to use power from the PoE power supply, if connected.

        - The 12 MP Box camera shall reboot and switch to the 12 VDC or 24 VAC power supply if power from the PoE power supply is lost.

      - The 12 MP Box camera shall offer Digital Wide Dynamic Range for clear images in extreme high-contrast environments.

      - The 12 MP Box camera shall offer the Intelligent Video System to detect and analyze moving objects for improved video surveillance.

      - The 12 MP Box camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.

      - The 12 MP Box camera shall offer three separate and configurable streams with individually configurable 12 MP, 4K and Full HD streams.

    - Imaging

      - The 12 MP Box camera shall offer a 1/1.7-inch type CMOS progressive-scan imager.

      - The 12 MP Box camera shall offer an effective number of pixels of 4000 x 3000 (12.0 MP) effective picture elements.

      - The 12 MP Box camera shall offer a 16:9 aspect ratio.

      - The 12 MP Box camera shall offer a maximum aperture of F1.2.

      - The 12 MP Box camera shall produce a color image with a minimum scene illumination of 0.01 lux at F1.2 and a monochrome image with a minimum illumination of 0.001 lux at F1.2.

    - Video Characteristics

      - The 12 MP Box camera shall offer CBR/VBR bit rate control.

      - The 12 MP Box camera shall offer the following video compression protocols

        - H.265 (14 to 9984 Kbps)

        - H.264 (24 to 16384 Kbps)

      - The 12 MP Box camera shall offer BLC, HLC, and Digital WDR modes of backlight compensation.

      - The 12 MP Box camera shall offer Auto, Natural, Street Lamp, Outdoor, and Manual modes.

      - The 12 MP Box camera shall offer 3D DNR noise reduction.

      - The 12 MP Box camera shall offer motion detection (four zones) and region of interest (four zones) controls.

      - The 12 MP Box camera shall offer four (4) privacy masking areas.

    - Streaming Capability

      - The 12 MP Box camera shall generate full 12 MP 
(4000 x 3000 pixels) at 20 fps resolution using H.265 compression.

      - The 12 MP Box camera shall offer Unicast and Multicast streaming methods.

      - The 12 MP Box camera shall offer the following resolutions:

        - 12 MP (4000 x 3000)

        - 4K (3840 x 2160)

        - 6 MP (3072 x 2048)

        - 5 MP (2560 x 1920)

        - 3 MP (2048 x 1536)

        - 3 MP (2304 x 1296)

        - 1080p (1920 x 1080)

        - 1.3 MP (1280 x 960)

        - 720p (1280 x 720)

        - D1 (704 x 480)

        - VGA (640 x 480)

        - CIF (352 x 240)

      - The 12 MP Box camera shall generate three streams at the following maximum resolutions:

        - Main Stream: 12 MP at 20 fps or 4K at 30 fps

        - Sub Stream 1: D1 at 30 fps

        - Sub Stream 2: 1080p at 30 fps

    - IP Connectivity

      - The 12 MP Box camera shall allow full camera control and configuration capabilities via a TCP/IP network.

      - The 12 MP Box camera shall deliver 12 MP video, at rates up to 20 frames per second via TCP/IP over an RJ-45 (100/1000 Base-T) connection.

      - The 12 MP Box camera shall conform to the ONVIF, PSIA, and the CGI standard.

      - The 12 MP Box camera shall offer Quality of Service (QoS) configuration options.

      - The 12 MP Box camera shall support the IPv6 internet-layer protocol for packet switched internetworking across multiple IP networks.

      - The 12 MP Box camera shall offer local and network storage options that include: MicroSD, Network Attached Storage (NAS), and recording to a local PC for instant recording.

      - The 12 MP Box camera shall support the following protocols: IPv4/ IPv6, HTTP, HTTPS, SSL, TCP/IP, UDP, UPnP, ICMP, IGMP, SNMP, RTSP, RTP, SMTP, NTP, DHCP, DNS, PPPOE, DDNS, FTP, IP Filter, QoS, Bonjour, and 802.1x.

      - The 12 MP Box camera shall support the Smart PSS and DSS management software.

      - The 12 MP Box camera shall support the Android and the IOS mobile operating systems.

    - Interface

      - The 12 MP Box camera shall offer one (1) audio input channel and one (1) audio output channel.

      - The 12 MP Box camera shall include a built-in microphone.

      - The 12 MP Box camera shall offer two (2) alarm input channels and one (1) alarm (relay) output channel.

      - The 12 MP Box camera shall offer one (1) RS485 connection.

      - The 12 MP Box camera shall offer one (1) auxiliary video output port.

    - Intelligent Video System

      - The 12 MP Box camera offer a built-in Intelligent Video System to provide advanced analytics for any scene.

      - The Intelligent Video System shall offer intelligent video analytics built-in to the 12 MP Box camera.

      - The Intelligent Video System shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.

      - The Intelligent Video System shall trigger an alarm and take a defined action for the following events:

        - Standard Features

          - Tampering with the camera.

          - Error writing to an onboard Micro SD Card.

          - Error sending or receiving data over the network.

          - Unauthorized access to the camera.

        - Premium Features

          - Motion: object moves through any part of the scene.

          - Tripwire: a target crosses a user-defined line.

          - Intrusion: a target enters or exits a defined perimeter.

          - Scene Change: a person or object moves the camera to change the scene or covers the camera to obscure the scene.

          - Abandoned/Missing Object: a target leaves an object in a designated area, or a target removes and object from the same designated area.

        - Advanced Features

          - Facial Detection: detects and captures a snapshot of a human face in a defined area within a scene.

          - Heat Map: generates a visual representation of data.

          - People Counting: measures the number of customers, visitors, or passengers in a surveillance scene.

    - Installation Requirements

      - The 12 MP Box camera shall be capable of operating in an outdoor environment within a temperature range of –30° C to +60° C (–22° F to 140° F).

      - The 12 MP Box camera shall accept power, transmit video, and accept control via a TCP/IP connection.

      - The 12 MP Box camera shall support the following dual, redundant power options:

        - 12 VDC or 24 VAC.

        - PoE (IEEE 802.3af, class 0).

        - The 12 MP Box camera shall default to use power from the PoE power supply, if connected.

        - The 12 MP Box camera shall reboot and switch to the 12 VDC or 24 VAC power supply if power from the PoE power supply is lost.

    - Housing Options

      - The 12 MP Box camera shall be offered in a metal housing.

  - ACCESSORIES

    - The 12 MP Box camera shall offer the following optional accessories:

      - [Wall mount.]

      - [Wall/Ceiling/Plane mount.]

- – EXECUTION

  - EXAMINATION

    - Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

    - Do not begin installation until unacceptable conditions are corrected.

  - PREPARATION

    - Protect devices from damage during construction.

  - INSTALLATION

    - Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.

    - Perform installation with qualified service personnel.

    - Install devices in accordance with the National Electrical Code or applicable local codes.

    - Ensure selected location is secure and offers protection from accidental damage.

    - Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - FIELD QUALITY CONTROL

    - Test snugness of mounting screws of all installed equipment.

    - Test proper operation of all video system devices.

    - Determine and report all problems to the manufacturer’s customer service department.

  - ADJUSTING

    - Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.

    - Make any adjustment of camera settings to comply with specific customer’s need.

  - DEMOSTRATION

    - Demonstrate at final inspection that video management system and devices functions properly.

END OF SECTION