Hanwha Techwin is a global leading supplier of solutions for IP and analog video surveillance. Building on the company's history of innovation, Hanwha Techwin is dedicated to providing systems solutions with the highest levels of performance, reliability and cost-effectiveness. Hanwha Techwin is committed to the continued development of innovative systems products for professional security applications.

# For additional information, visit http://www.hanwha-security.com/

2 MP ANALOG DOME CAMERA

# DIVISION 28 – ELECTRONIC SAFETY AND SECURITY

Notes to Specifier:

1.  Where several alternative parameters or specifications exist, or where, the specifier has the option of inserting text, such choices are presented in <bold text>.

2.  Explanatory notes and comments are presented in colored text.

Important:  See further notes on the following page.

# Important Note to Security Systems Specifiers

# CSI MasterFormat 2016 incorporates numerous significant changes affecting electronic safety and security. This document is written to provide flexibility in using either format, although adoption of MasterFormat 2016 is encouraged. The following is a guide to the MasterFormat numbers relevant to the product referenced in this specification.

# Primary Specification Area:

# MasterFormat 2014:

28 20 00 	Electronic Surveillance

28 23 00 	Video Surveillance

28 23 29	Video Surveillance Remote Devices and Sensors

MasterFormat 2016:

# 28 20 00	Video Surveillance

# 28 2x xx	Surveillance Cameras

# 28 2x xx	Analog Cameras

# Related Requirements:

# MasterFormat 2014:

# 27 20 00	Data Communications

# 28 23 13	Video Surveillance Control and Management Systems

# 28 23 16	Video Surveillance Monitoring and Supervisory Interfaces

# 28 23 19	Digital Video Recorders and Analog Recording Devices

# 28 23 23	Video Surveillance Systems Infrastructure

# MasterFormat 2016

# 27 15 01.xx	Video Surveillance Communications Conductors and Cables

# 27 20 00 	Data Communications

# 28 05 xx.xx	PoE Power Sources for Electronic Safety and Security

# 28 05 xx	Storage Appliances for Electronic Safety and Security

# 28 05 xx.xx	Network Video Recorders

# 28 05 xx	Cyber Requirements for Electronic Safety and Security

# 28 05 xx	Safety and Security Network Communications Equipment

# 28 2x 00	Video Management System

2 MP ANALOG DOME CAMERA

- GENERAL

  - SUMMARY

    - Section includes a 2 MP Analog video camera

    - Product – Analog HD dome camera  (AHD/CVI/TVI/CVBS output)

    - Related Requirements

Refer to MasterFormat notes at the beginning of this document to select requirements specific to the MasterFormat version being used in the specification.

  - REFERENCES

    - Abbreviations

      - ACP		AHD Coax Protocol

      - AGC		Auto Gain Control

      - AHD		Analog High Definition

      - AWB		Auto White Balance

      - BLC		Back light compensation

      - CCP		CVi Coax Protocol

      - CVBS		Composite Video Blanking and Sync

      - DNR		Digital Noise Reduction

      - fps		frames per second

      - GUI		Graphical User Interface

      - HD		High Definition

      - IR		Infrared

      - JPEG		Joint Photographic Experts Group

      - LED		Light Emitting Diode

      - LDC		Lens Distortion Correction

      - LPR		License Plate Recognition

      - MJPEG		Motion JPEG

      - MP		Megapixel

      - MPEG		Moving Pictures Experts Group

      - SDK		Software Development Kit

      - SFP		Small Form factor Pluggable

      - SSDR		Super Smart Dynamic Range

      - SSNR		Super Smart Noise Reduction

      - SSL		Secure Sockets Layer

      - TCP		TVi Coax Protocol

      - VMS		Video Management System

      - WDR		Wide Dynamic Range

    - Reference Standards

      - Emissions

        - FCC-47 CFR Part 15 Subpart B ANSI C63.4-2014, Class A

        - CE EN 55022:2010

        - IC Regulation ICES-003:2016 CAN/CSA CISPR 22-10 Class A

        - AS/NZS CISPR 32:2013 Class A

        - VCCI V-3/2015.04 Class A

      - Immunity - CE

        - EN 55032:2012/AC:2013 Class A

        - EN 50130-4:2011 +A1:2014

      - Safety

        - UL listed

      - CE EN 50581:2012 (hazardous substances)

  - SUBMITTALS

    - Product Data

      - Manufacturer’s printed or electronic data sheets

      - Manufacturer’s installation and operation manuals

      - Warranty documentation

  - QUALIFICATIONS

    - Manufacturer shall have a minimum of five years’ experience in producing video equipment.

    - Installers shall be trained and authorized by the Manufacturer to install, integrate, test, and commission the system.

  - DELIVERY, STORAGE AND HANDLING

    - Deliver the camera in the manufacturer’s original, unopened, undamaged container with identification labels intact.

    - Store the camera in a temperature environment specified in section 2.03 Detailed Specification, protected from mechanical and environmental conditions as designated by the manufacturer.

  - WARRANTY, LICENSING AND SUPPORT

    - Manufacturer shall provide at least a limited 3 year warranty for the product to be free of defects in material and workmanship.

    - Manufacturer shall provide embedded camera video analytics free of license charges.

END OF SECTION

- PRODUCTS

  - EQUIPMENT

    - Manufacturer: 	Hanwha Techwin

http://www.hanwha-security.com/

    - Model		HCD-6010

    - Alternates: 		None

  - GENERAL DESCRIPTION

    - Video and Transmission – The camera shall have the following properties relating to the video signals it produces.

      - 2 MP resolution, 30fps@1080p(N) / 25fps@1080p(P)

      - Video signals are output in AHD/TVi/CVi/CVBS(selectable) format via BNC terminal.

      - Video shall be able to be transmitted up to 500 meters with 5c2v cable.

    - Camera – The camera device shall have the following physical and performance properties:

      - True day/night operation with removable IR cut filter

        - Low light level operation to 0.27 lux at F2.0 in color mode and 0.017 lux in black and white mode.

      - The camera shall be able to produce clear images in highly contrast scenes with multi-exposure wide dynamic range up to 120dB.

      - The camera shall support digital noise reduction using SSNR4 technology.

      - The camera shall be able to configure 8 privacy masking areas with rectangles.

    - Intelligence and Analytics – The camera shall have a suite of intelligent analytic functions.

      - Motion detection with 4 definable detection areas.

      - Defog function

    - The camera shall be controlled by ACP, Coaxitron, CCP and TCP protocol.

  - DETAILED SPECIFICATIONS

    - Video

      - Imaging device			1/2.8" 2MP CMOS

      - Image Pixels			Total: 1,945(H) x 1,109(V), Effective: 1,945(H) x 1,097(V)

      - Scanning			Progressive

      - Resolution			1,920 x 1,080

      - Minimum Illumination		Color: 0.27Lux (F2.0, 1/30sec), B/W: 0.017Lux

      - S/N Ratio			52dB (AGC off, Weight on)

    - Lens:

      - Focal length			2.8mm fixed

      - Max. Aperture Ratio		F2.0

      - Field of View			H: 113.7˚,  V: 61.5°, D: 134.5°

      - Min. Object Distance		0.5m(1.64ft)

      - Lens Type			Fixed

      - Focus Control			Manual

      - Mount Type			Board-in Type

    - Pan & Tilt & Rotate

      - PTR Range			0˚~350˚ / 0˚~67˚ / 0˚~355˚

      - PTR Control			Manual

    - Operational Functions

      - On Screen Display		English, Spanish, French,  Portuguese, German, Italian, Russian,

Polish, Czech, Romanian, Serbian, Swedish, Danish, Turkish

      - Camera Title 			Off / On (Displayed up to 15 characters)

      - Day/Night Setting		Auto (ICR) / Color / B/W

      - Backlight Compensation		Off / User BLC / HLC / WDR

      - WDR				120dB

      - Digital Noise Reduction		SSNR4 (Off/ On)

      - Super Smart Dynamic Range	Off / On

      - Defog				Auto / Manual / Off

      - Motion Detection		Off / On (4 zones)

      - Privacy Masking		Off / On (8 zones, rectangular)

      - Gain Control			Off / Low / Middle / High / Very High

      - White Balance 			ATW / Outdoor / Indoor / Manual / AWC

      - Electronic Shutter Speed 	1 sec ~ 1/12,000sec

      - Reverse			Off / H-Rev /V-Rev /HV-Rev

      - Profile				Basic / Day & Night / Backlight / ITS / Indoor / User

      - Remote Control Interface	Coaxial

      - Protocol			AHD: ACP(AHD Coax Protocol), CVBS: Pelco-C (Coaxitron)

CVi: CCP (CVi Coax Protocol), TVi: TCP (TVi Coax Protocol)

      - Video Transmission Distance	500 m (5c2v)

    - Electrical

      - Input Voltage			DC 12V ± 10%

      - Power Consumption		3.6 W

    - Mechanical and

      - Color/Material			Ivory / Plastic

      - Dimensions (W x H)		Ø110 x 86 mm (Ø 4.33" x 3.39")

      - Weight 				221g (0.49 lb)

    - Environmental

      - Operating Temperature		-10°C ~ +50°C(+14°F ~ +131°F)

      - Operating Humidity		Less than 90% RH

END OF SECTION

- EXECUTION

  - INSTALLERS

    - Contractor personnel shall comply with all applicable state and local licensing requirements.

  - PREPARATION

    - The design and configuration shall be verified for compatibility and performance with the camera(s).

    - Configuration shall be tested and qualified by the Contractor prior to camera installation.

    - All firmware found in products shall be the latest and most up-to-date provided by the manufacturer, or of a version as specified by the provider of the Video Management Application (VMA) or Digital Video Recorder (DVR).

  - INSTALLATION

    - The Contractor shall carefully follow instructions in documentation provided by the manufacturer to insure all steps have been taken to provide a reliable, easy-to-operate system.

    - All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

    - Before permanent installation of the system, the Contractor shall test the system in conditions simulating the final installed environment.

  - STORAGE

    - The camera hardware shall be stored in an environment where temperature and humidity are in the range specified by the Manufacturer.

END OF SECTION

10